## Slide 1: Chemical Treatment

## Slide 2: Types of Treatment
Sedimentation
  Physical
  Chemical
Disinfection

## Slide 3: Physical Sedimentation
Keeping the water in a tank long enough for the dirt to settle to the bottom

## Slide 4: Chemical Sedimentation

## Slide 5: Jar Test
Place different quantities of alum in different containers of water.
Measure turbidity at regular time intervals.
Choose the best dosage.
Convert dosage to the tank you are using

## Slide 6: Turbidity
Turbidity is how clear the water is.
Turbidity of drinking water must be less than 5 NTU

## Slide 7: Example
You do a jar test in several 15 litre buckets. 2 grams of alum is the best dosage.
You are treating water in a T45 (45,000 litres).
How much alum per batch do you add?

## Slide 8: Solution
2 grams for 15 litres
45,000 litres / 15 litres = 3,000
2 grams x 3,000 = 6,000 grams or 6 kilograms

## Slide 9: Disinfection
Adding chlorine to water in order to kill any harmful organisms.
Adding chlorine to provide residual protection.

## Slide 10: How much chlorine?
Enough to kill harmful organisms
Not so much that people dislike the taste
Sphere standard 0.5 mg/L
Test with pool tester
Select dosage with bucket test

## Slide 11: Bucket Test
Place different quantities of 1% chlorine solution in different containers of water.
Measure chlorine after 30 minutes.
Choose the best dosage.
Convert dosage to the tank you are using

## Slide 12: Making 1% chlorine solution
1 spoon of HTH powder is about 14 grams
HTH powder is 70% chlorine
So 1 spoon of HTH powder is 10 grams chlorine
1 litre is 1kg or 1000g
So 10 grams of chlorine in 1000 grams of water is 1%

## Slide 13: Example
You do a bucket test in several 15 litre buckets. 5 ml of 1% solution is the best dosage.
HINT: There is 10 g of chlorine in 1 litre of 1% solution or 0.01 g per mL
You are treating water in a T45 (45,000 litres).
How much chlorine per batch do you add?

## Slide 14: Solution
0.01 g chlorine per mL of 1% solution
so 0.05 g chlorine in 5 ml
45,000 litres / 15 L = 3,000
3,000 x 0.05 g = 150 g
1 spoon = 10 g
So, 15 spoons