## Slide 1: INNOVATIVE SANITATION OPTION in URBAN CONTEXT Bio-Digester Technology for Safer Sanitation M1512005
AMAR MANI POUDEL Deputy Director NEPAL RED CROSS SOCIETY

## Slide 2
Bio-Digester Technology for Safer Sanitation M1512005
Partnership between
Gates Foundation and International Red Cross and Red Crescent societies (IFRC)
Implementing By:

## Slide 3
Trial Households :
Ishwor Tiwari
Sudarshan Aryal
Ram Chandra Lama
Raj Kumar Lama
All are 2015 EQs affected households

## Slide 4: TECHNOLOGY :
Researched by the scientists of the Defense Research and Development Organization (DRDO), through the Government of India (GoI)
A consortium of bacteria of which some is from Antarctica
This consortium of bacteria converts human waste to methane, carbon dioxide and water
The effluents is claimed to be 99% pathogen free (DRDO Claim)
The technology has claimed to have worked well over a wide range of temperatures between -50 0C to +50 0C

## Slide 5: Family Toilet (5-6 members) : Approx. 220 Lt Inoculum used @ CHF 0.9 excluding transport
Cow dung as inoculum carrier
Inoculum factory
Transported by road from India to Nepal

## Slide 6: Bio-Digester Tank Design- Brick Masonry 1m3 capacity
The design was approved by DRDO

## Slide 8: Bio-digester Tank-Brick Masonry

## Slide 10: Test Frequency of Affluent Water

## Slide 11: Parameters of effluent Water Testing
PARAMETERS
pH
Turbidity
Suspended Solids
Total Dissolved Solids
Total Volatile Solids
Chemical Oxygen Demand
Biochemical Oxygen Demand for 5 days
Dissolved Oxygen
Ammonia as NH3
Total Coliform (MPN)
E.Coli

## Slide 12: Test Results-H1 Ram Chandra Lama
S.N | Parameter | Unit | Standard | Result (T1) | Result (T2) | Result (T3)
1 | Total Suspended solids | Mg/l | 30-200 | 284.0 | 340.0 | 306.0
2 | Total Dissolved solids | Mg/l | - | 949 | 293.0 | 930.0
3 | Total Volatile solids | Mg/l | - | 190 | 275.0 | 166.0
4 | PH |  | 5.5-9 | 7.8 | 7.3 | 7.3
5 | Field Temperature | oC | <40 | 23.2 | 27.2 | 22.2
6 | Turbidity | NTU | - | 464.0 | 435.0 | 405.0
7 | BOD | Mg/l | 30-100 | 271.0 | 59.0 | 121.0
8 | COD | Mg/l | 250 | 627.4 | 126.0 | 291.0
9 | Dissolved Oxygen | Mg/l | - | <0.1 | <1.0 | <1.0
10 | Ammonia | Mg/l | 50 | 80.4 | 36.0 | 98.2
11 | Total Coliforms | MPN/100ml | - | 2x106 | 6x106 | 6x105
12 | E. Coli | 0 org/100ml | - | 2x103 | 3x105 | 3x105
13 | Ascaries Lumbricoids | 0 org/100ml | - | Unfertilized egg seen | Not seen | Not seen

## Slide 13: Test Results-H2 Raj Kumar Lama
S.N | Parameter | Unit | Standard | Result (T1) | Result (T2) | Result (T3)
1 | Total Suspended solids | Mg/l | 30-200 | 678.0 | 1684.0 | 1720.0
2 | Total Dissolved solids | Mg/l | - | 2493 | 2513.0 | 2444.0
3 | Total Volatile solids | Mg/l | - | 448.0 | 830.0 | 826.0
4 | PH |  | 5.5-9 | 8.1 | 7.8 | 8.0
5 | Field Temperature | oC | <40 | 23.4 | 27.1 | 22.29
6 | Turbidity | NTU | - | 1112.0 | 725.0 | 877.0
7 | BOD | Mg/l | 30-100 | 1320.0 | 2484.0 | 988.4
8 | COD | Mg/l | 250 | 3019.6 | 1027.0 | 2435.6
9 | Dissolved Oxygen | Mg/l | - | 0.2 | <1.0 | <1.0
10 | Ammonia | Mg/l | 50 | 708.7 | 1443.0 | 619
11 | Total Coliforms | MPN/100ml | - | 2x106 | 2x106 | 3x105
12 | E. Coli | 0 org/100ml | - | 2x105 | 3x106 | 1.4x103
13 | Ascaries Lumbricoids | 0 org/100ml | - | Not seen | Not seen | Not seen

## Slide 14: Test Results-H3 Ishwar Tiwari
S.N | Parameter | Unit | Standard | Result (T1) | Result (T2) | Result (T3)
1 | Total Suspended solids | Mg/l | 30-200 | 289.0 | 265.0 | 270.0
2 | Total Dissolved solids | Mg/l | - | 1396.0 | 1437.0 | 524.0
3 | Total Volatile solids | Mg/l | - | 182.0 | 131.0 | 134.0
4 | PH |  | 5.5-9 | 7.6 | 7.5 | 7.1
5 | Field Temperature | oC | <40 | 23,8 | 27.1 | 22.9
6 | Turbidity | NTU | - | 474.0 | 325.0 | 175.0
7 | BOD | Mg/l | 30-100 | 459.0 | 192 | 99.9
8 | COD | Mg/l | 250 | 1019.6 | 468.0 | 136.0
9 | Dissolved Oxygen | Mg/l | - | <0.1 | <1.0 | <1.0
10 | Ammonia | Mg/l | 50 | 145.4 | 185.6 | 50.15
11 | Total Coliforms | MPN/100ml | - | 1x106 | 4x106 | 1x106
12 | E. Coli | 0 org/100ml | - | 2.5x105 | 1.5x105 | 3x105
13 | Ascaries Lumbricoids | 0 org/100ml | - | Not seen | Not seen | Not seen

## Slide 15: CHALLENGES
Approval by Nepal Government for Inoculum transportation from India to Nepal
Appropriate site selection for trials (1st tried in slum area only with cow dung )

## Slide 16: Lesson Learnt so far
Households selection for bio-digester toilet
Do and Don’t for households (users)
Trial of Blander tank (NVH Technology)

## Slide 17: Way Forward
Trial for institutional toilet (for hospital, public toilet etc.) in next phase
Appropriate selection of Households
Beforehand orientation to users (Do & Don’t)
Revision of design-HH type ?
Reed bed management for affluent water
Lobby for licensing for inoculum production and selling in Nepal

## Slide 18: Types of FRP and MTM digester tanks

## Slide 19: THANK YOU