## (Partially adapted from Engineering in Emergencies: A Practical Guide for Relief Workers  Chapter 14 by Jan Davis & Robert Lambert 2nd Edition 2002)

## WATER PUMPS

1. Physical principles of pumping

Pumps are used to lift water against gravity or to pressurize water sufficiently to move it through a pipeline at a desire rate.

Pumps are rated according to the flow rate of water which can be pumped against a certain pressure or “head”, at a given operating speed.

a) Total head (H)

The total pressure head which a pump must overcome is composed of static and friction heads.

Static head

The static head is the total vertical height through which the water is to be pumped. This is made up of the static suction head Hss and the static delivery head Hsd. Note that the static suction head, whereas the static delivery head

Static suction head (Hss)

It is the vertical height from the pump inlet to the surface of water, not to the bottom of the pipe.

Static delivery head (Hsd)

It is the vertical height from the pump outlet to the outlet of the delivery pipe.

Friction head (Hfd)

The head required to overcome friction in the system (pipes and fittings) is the friction head loss.

b) Suction lift

To raise water from below the level of the pump, a partial vacuum (a pressure less than atmospheric) must be created in the suction pipe. When the pipe is inserted in an open body of water, atmospheric pressure causes the water to flow into the pipe. The theoretical maximum lift for a perfect vacuum is 10.35 m (atmospheric pressure at 0ºC and sea level). This is reduced by about 1 m for every 1000 m above sea level. However, the actual maximum suction lift is less, because energy is used to move water and to overcome resistance to flow.

The suction lift height of the pump is 6 m. maximum. Although the length of the suction pipe is 8 m., it cannot be disposed totally vertical (90º). As shown above, the creation of a partial vacuum is what impels water to circulate (a pressure below atmospheric) when the suction pipe is inserted in water due to the atmospheric pressure being higher than the internal pressure in the pipe which will impel water to circulate.

When the delivery head is higher than the capacity of the pump it will be necessary to dispose a middle tank from where water can be pumped to the water treatment plants.

2. Pump power calculation

The hydraulic power of a pump is expressed through the following mathematical formula:

P = Power requirement (w).

Q = Flow rate of water (l/s).

H = Operating pressure head against which the pump must discharge (m).

η  = Overall efficiency

ρ  = Density of water (1.0 kg/l)

g  = Gravitational acceleration (9. 8 m/s2)

As the density of water (ρ) and gravitational acceleration are constants, the power is a constant relationship between H, Q, and η. The relationship between these three variables gives rise to the typical curve of each pump which graphically allows obtaining the flow related to a certain total head or vice versa.

Transmission efficiencies may be up to 90% for close couple electric motors and may be about 65% for belt drives from internal combustion (IC) engines. Maximum centrifugal pump efficiencies are about 70-80 per cent but may be much lower than this. Combining the transmission losses and pump losses gives typical efficiencies of 40-60 percent. A centrifugal pump delivering 2.5 kW and powered by an IC engine will typically require 5.0 kW from engine.

3. Pump classification

Most pumps can be classified as a) rotodynamic b) positive displacement pumps.

Rotodynamic pumps use a rotor or impeller rotating inside a casing. The most common is the centrifugal pump either single-stage or multi-stage which in turn can be surface mounted or submergibles.  Pump discharge rates vary considerably with the head against which the water is being pumped.

Positive displacement pumps involve a dumping element (such as a piston or helical rotor) displacing a fixed amount for each cycle of the pump.

4. Centrifugal pumps

a) Single stage surface mounted pumps

Centrifugal pumps are by far the most common type of rotodynamic pump, and they are used in many applications. A single impeller inside a chamber forms the basic single-stage centrifugal pump. High-speed rotation of the impeller causes water to be sucked into the eye and thrown radially, emerging through the outlet under pressure. The functioning principle is shown in the following figure.

Installation

Site pumps upstream of bathing, washing and animal watering areas. If the water source is a river, a good pump site has:

    - A firm bank that is not likely to be washed away.

    - A reasonable depth of water close to the bank.

    - A bankside which is free of silt, weed and grass

Choose a pump site which keeps the length of the dumping main to a minimum and provides a gradual incline to the storage tanks. Avoid dips and peaks in a pipeline. Silts can settle out in a dip when water in the pipe is stationary. Air can be trapped in a peak and cause pumping problems.

The position and arrangement of the suction inlet is critical to avoid pumping silt and to prevent the ingress of weeds, leaves and debris. Keep suction lifts and lengths of suction pipe to a minimum. We must remember that the usual maximum vertical length of suction is 6 metres.  Submerge the inlet of the suction pipe a sufficient depth ( at least 0.3 m) to prevent the formation of vortices, which can entrain air and adversely affect pump performance. When the pump is running at full speed, check for such vortices.

Sand or silt will rapidly damage most pumps irreparably. Therefore, take great care to minimize sand or silt ingress into the pump:

    - Never allow a suction inlet to sit on the bottom of a lake or river bed.

    - Fit a means of excluding silt or suspend the inlet at least 0.3 m above the bottom of the source, or at the minimum, position it on rock, a board or similar.

To prevent blockage of the suction pipe by vegetation, fit a strainer.

Operation

When installing and operating a surface mounted centrifugal pump:

- Prime the pump before starting.

- Never run the pump dry.

- Start against a closed valve.

- Check you have enough spares in case the pump breaks down.

- Prime a centrifugal pump before starting

A centrifugal pump canny pump air alone and therefore, when the suction head is negative, it must be prime with water before it can function as a pump.  Even when the pump is self-priming it is very advisable to prime the pump. This will prolong the life-span of the pump and will prevent from the device being overloaded.

- Never run a pump dry

Pump seals, an some bearings, can be damaged if they run without water. Therefore, always pour water into the pump chamber and run a pump “wet”, even when testing prior to installation.

c)     Start against a closed valve

The power required by a centrifugal pump is at a minimum when there is no flow. Therefore, although it may not be immediately obvious, it is better to start a centrifugal pump against a closed valve to reduce the power required on start-up. It is a good practice for the operator to close the delivery valve just before the pump is stopped so that the pump is ready to re-start against a closed valve. This also has the advantage of relieving pressure of the head of the water in the main on the non-return valve and pump components.

- Multiple stage pumps

A multi-stage pump consists of several stages placed one after the other on the same shaft. The arrangement is equivalent to a number of individual centrifugal pumps in series. The flow remains constant, but the pressure head developed is increased at each stage. Multi-stage pumps are commonly used a) for boosting of water pressure and b) in submergible pumps. Multi-stage centrifugal pumps, particularly submergibles, are manufactured to very close tolerances, and can be easily damaged and will block very easily. They will only pump very clean water.

- Water hammer

Water hammer (or, more generally, fluid hammer) is a pressure surge or wave resulting when a fluid in motion is forced to stop or change direction suddenly (momentum change).

Water hammer commonly occurs when a valve is closed suddenly at an end of a pipeline system, and a pressure wave propagates in the pipe.

Water hammer occurs:

- When a valve is open or closed suddenly.

- When a hydraulic machine starts against a closed valve.

- When there is a sudden variation of the flow.

- When a hydraulic machine stops and there is a high pressure during the discharge.

5. WATSAN M15 ERU pumps

Lombardini LDP4045 diesel. Single-stage surface mounted centrifugal pump.

Honda WB20XT petrol. Single stage surface mounted centrifugal pump.

Espa Mod. Prisma 15 electric. Multi-stage surface mounted centrifugal pump with hydroneumatic group (pressure group).

Grundfos Mod. MQ 3-45 electric. Surface mounted centrifugal pump with pressure tank and control. SETA water treatment plant.

Lowara electric. Multi-stage submergible centrifugal pump. SETA water treatment plant.

EMEC Mod. HMS-CO 05-05 electric. Dosing pump. SETA water treatment plant.

# Text boxes

Friction Head (Hfd)

Static Delivery Head

(Hsd)

Static Suction Head (Hss)

Total Head

(H)

Maximum lifting level

Water source

Tank

Pump

Drawing of a multi-stage centrifugal submergible pump.

This pump is used, as part of the water abstraction submodule, to pump water from the water source to the pretreatment open tanks (30,000 or 10,000 litres) for specialized water. Also to pump water to same tanks when they are not used for pretreatment but for treatment as mass water which excludes mobile water treatment plants.

Characteristics: 0.9 kW / 220 V / 50 HZ Diesel

Max. Flow: 40 m3 / h

Max. Lifting: 45 m

3” Storz coupling (Inlet and outlet)

Self-priming pump

This pump is used, as part of the distribution submodule, to transfer water between tanks and particularly for the 5,000 litre bladder tanks transported in lorries.

Engine GX120 3.1 litres

Range 1.9 h

Max. Lifting: 32 m

Max. Flow: 36m3/h

Measurements: 470 x 350 x 380 mm

Weight:  25 Kg

2” coupling (inlet & outlet)

Self-priming: 110 seconds @ 5 m

FLOW AND TOTAL HEAD

Static Delivery Head (Hsd): 8 m

-    36 m3/h @ 10 m.  H

-    24 m3/h @ 20 m.  H

-      9 m3/h @ 25 m.  H

This pump and pressure group is used, as part of the pipeline submodule, to provide pressurized water to hospitals, heath centres or IDP Camps. Drinking water is suctioned from static tanks bladder-type (10,000 or 5,000 litres), OXFAM (10,000 litres or more) or others.

Characteristics: 0.5 CV / 0.37 KW. 220 V,

50 Hz.

Weight: 9 Kg

1” Storz coupling (Inlet & outlet)

Self-priming up to 2 m.

FLOW AND TOTAL HEAD

0.6 m3/h @ 32 m H

1.2 m3/h @ 30 m H

1.8 m3/h @ 26 m H

2.4 m3/h @ 22 m H

3.0 m3/h @ 17 m H

3.6 m3/h @ 10.5 m H

3.9 m3/h @   6 m H

This pump and pressure group is installed in the SETA water treatment plant. Its function is to deliver pressurized water to the filters and to the storage tanks at the end of the process.

Characteristics: 1 KW, 220 V, 50 Hz.

Weight: 13 Kg.

Max. Flow: 4.5 m3/h

This pump is a component of the SETA water treatment plant. Its function is to pump raw water to the plant for its treatment.

Characteristics: 0,9 Kw, 220 V, 50 Hz.

This dosing pump is installed in the SETA WTP. Its function is to pump Chlorine and Aluminium Sulphate solutions to the water treatment system. There are three similar pumps in the plant.

Characteristics: 18.4 w, 220 V, 50 Hz.

Maximum Flow: 5 litres/h

To prime, remove the priming plug and fill the pump chamber and suction pipe with water. For a more rapid process, we can decouple the suction pipe, fill it out with water and couple it again to the pump.

PRIMING PLUG

Detail of ESPA Mod. Prisma15 horizontal multi-stage centrifugal pump for a pressure group

SETA WTP Grundfos Mod. MQ 3-45 centrifugal pump maximum lifting height.